## Dispersant Dosing
Parameter | Amount
ppm. Range | 50-100 | Note :
Selected.ppm | 100 | 1) | The tank shall be full in 1 hr,based on this data loading pump capacity will be selected.
Blow Down Water (m3/hr) | 89.8 | 2) | Discharge pressure for loading pump is 1 barg.
Dispersant Consumption per hr (Kg/hr) | 8.98 | 3) | The tank needs 1 Mixer.
Dispersant Consumption per day (Kg/day) | 215.52 | 4) | The package have been equiped with 2 dosing pump (1+1).
Dispersant Consumption per day (Kg/month) | 6465.6 | 5) | Discharge pressure of dosing pumps are 3 bar.
density (Kg/Lit) | 1 | 6) | One storage tank for 7 days consumption has been considered. | ???
Volumetric Dispersant Dosing Rate (Lit/hr) | 9 |  | Input Data
Volumetric Dispersant Dosing Rate (Lit/day) | 216 |  | Calculated Data
Volumetric Dispersant Dosing Rate (Lit/Week) | 1512 |  | Reference Data
Selected Storage Capacity (Lit) | 2000

## Sheet2
Parameter | Amount
ppm. Range | 50-100
Selected.ppm | 100
Blow Down Water (m3/hr) | 89.8
Dispersant Consumption per hr (Kg/hr) | 8.98
Dispersant Consumption per day (Kg/day) | 215.52
density (Kg/Lit) | 1
Volumetric Dispersant Dosing Rate (Lit/hr) | 9
Volumetric Dispersant Dosing Rate (Lit/day) | 216
Volumetric Dispersant Dosing Rate (Lit/3days) | 648
10% overdesign has been considered | 712.8
Selected Storage Capacity (Lit) | 1000

## Corrosion Inhibitor
Parameter | Amount
ppm. Range | 50-150 | Note :
Selected.ppm | 150 | 1) | The tank shall be full in 1.5 hr,based on this data loading pump capacity will be selected.
Blow Down Water (m3/hr) | 89.8 | 2) | Discharge pressure for loading pump is 1 barg.
Corrosion Inhibitor Consumption per hr (Kg/hr) | 13.47 | 3) | The tank needs 1 Mixer.
Corrosion Inhibitor Consumption per day (Kg/day) | 323.28 | 4) | The package have been equiped with 2 dosing pump (1+1).
Corrosion Inhibitor Consumption per day (Kg/month) | 9698.4 | 5) | Discharge pressure of dosing pumps are 3 bar.
density (Kg/Lit) | 1 | 6) | One storage tank for 7 days consumption has been considered. | ???
Volumetric Corrosion Inhibitor Dosing Rate (Lit/hr) | 14 |  | Input Data
Volumetric Corrosion Inhibitor Dosing Rate (Lit/day) | 336 |  | Calculated Data
VolumetricCorrosion Inhibitor Dosing Rate (Lit/Week) | 2352 |  | Reference Data
10 % over design has been considered for loss (Lit) | 2587.2
Selected Storage Capacity (Lit) | 3000

## Sheet1
Parameter | Amount
ppm. Range | 50-150
Selected.ppm | 150
Blow Down Water (m3/hr) | 89.8
Corrosion Inhibitor Consumption per hr (Kg/hr) | 13.47
Corrosion Inhibitor Consumption per day (Kg/day) | 323.28
density (Kg/Lit) | 1
Volumetric Corrosion Inhibitor Dosing Rate (Lit/hr) | 14
Volumetric Corrosion Inhibitor Dosing Rate (Lit/day) | 336
VolumetricCorrosion Inhibitor Dosing Rate (Lit/3days) | 1008
10 % over design has been considered for loss (Lit) | 1108.8
Selected Storage Capacity (Lit) | 1500

## Biocide -Shock Dose
Parameter | Amount
ppm. Range | 100 | Note :
Selected.ppm | 100
Water hold in piping and basin (m3) | 13000 | 1) | Discharge pressure for loading pump is 1 barg.
Circulating Water (m3/hr) | 30000 | 2) | The tank needs 1 Mixer.
Retention Time (min) (Hold up Water/Circulating Water) | 26 | 3) | The package have been equiped with 2 dosing pump (1+1).
Biocide Consumption (Kg) | 1300 | 4) | Discharge pressure of dosing pumps are 3 bar.
Mass Flow Rate for Dosing pump in Retention Time (Kg/hr) | 3000
Mass Flow Rate for Dosing pump in 240 min (Kg/hr) | 325 |  | Input Data
Pump Capacity (Kg/hr) | 325 |  | Calculated Data
density (Kg/Lit) | 1 |  | Reference Data
Biocide Dosing Rate (Kg/hr) | 325
Volumetric Biocide Dosing Rate (Lit/hr) | 325
Selected Storage Capacity (Lit) | 1000

## Biocide -SodiumHypochlorite
Parameter | Amount
ppm. Range | 0.3-0.5 | Note :
Selected.ppm | 0.5 |  | Ca(ClO)2- 10%-NaOCl 10% | NaOCl | محلول
Circulating Water (m3/hr) | 30000 | 2) | The tank needs 1 Mixer. | CaOCl | پودر
Hypochlorite Consumption (Kg/hr) | 150 | 3) | The package have been equiped with 2 dosing pump (1+1).
Hypochlorite Consumption per day (Kg/day) | 3600 | 4) | Discharge pressure of dosing pumps are 3 bar.
Hypochlorite Consumption per week (Kg/week) | 25200
density (Kg/Lit) | 1 |  | Input Data
Volumetric Consumption of Hypo per week (lit/hr) | 25200 |  | Calculated Data
Selected Storage Capacity (Lit) | 30000 |  | Reference Data

## Sheet3
Parameter | Amount
ppm. Range | 0.3-0.5
Selected.ppm | 0.5
Circulating Water (m3/hr) | 30000
Hypochlorite Consumption (Kg/hr) | 150
Hypochlorite Consumption per day (Kg/day) | 3600
Hypochlorite Consumption per 3days (Kg/3days) | 10800
density (Kg/Lit) | 1
Volumetric Consumption of Hypo (lit/3days) | 10800
10% over design has been considered | 11880
Selected Storage Capacity (Lit) | 12000

## Sodium Carbonate
Parameter | Amount |  | Sodium Carbonate Or Calcium Hydroxide-20%
ppm. Range | 40-60 | Note :
Selected.ppm | 40
Blow Down Water (m3/hr) | 89.8 | 1) | The tank shall be full in 1 hr,based on this data loading pump capacity will be selected.
Sodium Carbonate Consumption per hr (Kg/hr) | 17.96 | 2) | Discharge pressure for loading pump is 1 barg.
density (Kg/Lit) | 1 | 3) | The tank needs 1 Mixer.
Volumetric Dispersant Dosing Rate (Lit/hr) | 18 | 4) | The package have been equiped with 2 dosing pump (1+1).
Volumetric Dispersant Dosing Rate (Lit/day) | 432 | 5) | Discharge pressure of dosing pumps are 3 bar.
Volumetric Dispersant Dosing Rate (Lit/Week) | 3024 | 6) | One storage tank for 7 days consumption has been considered. | ???
Selected Storage Capacity (Lit) | 3500 |  | Input Data
Calculated Data
Reference Data

## Sheet4
Parameter | Amount
ppm. Range | 40-60
Selected.ppm | 40
Blow Down Water (m3/hr) | 89.8
Sodium Carbonate Consumption per hr (Kg/hr) | 17.96
density (Kg/Lit) | 1
Volumetric Sodium Carbonate Rate (Lit/hr) | 18
Volumetric Sodium Carbonate Dosing Rate (Lit/day) | 432
Volumetric Sodium Carbonatet Dosing Rate (Lit/3days) | 1296
10% over designe has been considered | 1425.6
Selected Storage Capacity (Lit) | 1500