## COVER SHEET
Owner: |  |  | PARS PETROCHEMICAL COMPANY | [7 empty] | Contractor:
PROPANE DEHYDROGENATION (PDH) PROJECT
Duty Specification for Sodium Carbonate Dosing Package (81-W-505)
MC:
Document Number: |  |  | Project Code |  | Sec. | Phase Code | Department | Doc. Type | Serial No. |  | Rev.: |  | Page
|  |  | 3981-50-DE-PR-DSP-018 | [7 empty] | 07 |  | 1 of 6
Duty Specification for Sodium Carbonate Dosing Package (81-W-505)
07 | 2025-09-27 | Final Issue | [5 empty] | M.Fallahi |  | M.Jamshidi |  | M.H.Eshraghi
06 | 2025-08-25 | Final Issue | [5 empty] | M.Fallahi |  | M.Jamshidi |  | M.H.Eshraghi
05 | 2025-05-07 | Final Issue | [5 empty] | M.Fallahi |  | M.Jamshidi |  | M.H.Eshraghi
04 | 2025-02-26 | Issued For Approval | [5 empty] | M.Fallahi |  | M.Jamshidi |  | E.Shafaghati
03 | 2025-01-27 | Issued For Approval | [5 empty] | M.Fallahi |  | M.Jamshidi |  | E.Shafaghati
02 | 2024-05-11 | Issued For Approval | [5 empty] | M.Afsar |  | A.Hadipour |  | A.Aghaei
01 | 2023-12-25 | Issued For Approval | [5 empty] | M.Afsar |  | A.Hadipour |  | A.Aghaei
00 | 2023-11-22 | Issued For Approval | [5 empty] | F.Ebrahimi |  | A.Hadipour |  | D.Mirblouki
Rev. | Date | Purpose of Issue | [5 empty] | Prepared |  | Checked |  | Approved
Class: 1

## REVISION INDEX (2)
Owner: | [6 empty] | PARS PETROCHEMICAL COMPANY | [13 empty] | Contractor:
PROPANE DEHYDROGENATION (PDH) PROJECT
Duty Specification for Sodium Carbonate Dosing Package (81-W-505)
MC:
Document Number: | [6 empty] | Project Code |  |  | Sec. | Phase Code |  |  | Department |  |  | Doc. Type |  |  | Serial No. | Rev.: 07 |  |  |  | Page: 2 of 6
3981-050-DE-PR-DSP-018
TABULATION OF REVISED PAGES
Page | Revision | [7 empty] | Page |  |  | Revision | [7 empty] | Page | Revision
| 00 | 01 | 02 | 03 | 04 | 05 | 06 | 07 |  |  |  | 00 | 01 | 02 | 03 | 04 | 05 | 06 | 07 |  | 00 | 01 | 02 | 03 | 04 | 05 | 06 | 07
1 | [8 empty] | 37 | [10 empty] | 73 | bar: Revision 00 to Revision 07
2 | [8 empty] | 38 | [10 empty] | 74 | bar: Revision 00 to Revision 07
3 | [8 empty] | 39 | [10 empty] | 75 | bar: Revision 00 to Revision 01; Revision 03; Revision 05
4 | [8 empty] | 40 | [10 empty] | 76 | bar: Revision 00 to Revision 01; Revision 03 to Revision 05
5 | [8 empty] | 41 | [10 empty] | 77 | bar: Revision 00 to Revision 01; Revision 03 to Revision 06
6 | [8 empty] | 42 | [10 empty] | 78 | bar: Revision 00 to Revision 03; Revision 05
7 | [8 empty] | 43 | [10 empty] | 79
8 | [8 empty] | 44 | [10 empty] | 80
9 | [8 empty] | 45 | [10 empty] | 81
10 | [8 empty] | 46 | [10 empty] | 82
11 | [8 empty] | 47 | [10 empty] | 83
12 | [8 empty] | 48 | [10 empty] | 84
13 | [8 empty] | 49 | [10 empty] | 85
14 | [8 empty] | 50 | [10 empty] | 86
15 | [8 empty] | 51 | [10 empty] | 87
16 | [8 empty] | 52 | [10 empty] | 88
17 | [8 empty] | 53 | [10 empty] | 89
18 | [8 empty] | 54 | [10 empty] | 90
19 | [8 empty] | 55 | [10 empty] | 91
20 | [8 empty] | 56 | [10 empty] | 92
21 | [8 empty] | 57 | [10 empty] | 93
22 | [8 empty] | 58 | [10 empty] | 94
23 | [8 empty] | 59 | [10 empty] | 95
24 | [8 empty] | 60 | [10 empty] | 96
25 | [8 empty] | 61 | [10 empty] | 97
26 | [8 empty] | 62 | [10 empty] | 98
27 | [8 empty] | 63 | [10 empty] | 99
28 | [8 empty] | 64 | [10 empty] | 100
29 | [8 empty] | 65 | [10 empty] | 101
30 | [8 empty] | 66 | [10 empty] | 102
31 | [8 empty] | 67 | [10 empty] | 103
32 | [8 empty] | 68 | [10 empty] | 104
33 | [8 empty] | 69 | [10 empty] | 105
34 | [8 empty] | 70 | [10 empty] | 106
35 | [8 empty] | 71 | [10 empty] | 107
36 | [8 empty] | 72 | [10 empty] | 108

## Content
OWNER: |  |  | Pars Petrochemical Company | [5 empty] | contractor:
PROPANE DEHYDROGENATION (PDH) PROJECT
Duty Specification for Sodium Carbonate Dosing Package (81-W-505)
MC:
|  |  | Project code | Sec. | Phase Code | Department | Doc Type | Serial No.
Document Number : |  |  | 3981-050-DE-PR-DSP-018 | [5 empty] | Rev: | Page:
[9 empty] | 07 | 3 of 6
1 | Note | General Information | [8 empty] | Rev
2 |  | Project Description
3 |  | Project Description Pars Petrochemical Company intends to build Propane Dehydrogenation (PDH) Plant for Producing Propylene as Product near Bushehr, Pars Petrochemical Company, Iran. EPCC Contractor for PDH plant: Bina EPC Contractor-Panah Sanat Part Company. Main product is 600 KTY Propylene. The plant is to produce Propylene comprises of several main process units, including Feed preparation, Reaction Trains, Gas Compression, CO2 Removal, Separation and Fractionation.
4
5
6
7 |  | Injection Package Description
8 |  | This document defines the process basic requirement for the design and supply of Sodium Carbonate Dosing Package for PDH. The Sodium Carbonate Dosing Package has to be utilized in cooling water basin for raise the PH of water and PH adjustment of water.
9 |  | Chemical media will be stored in storage tank. The chemical storage tank shall have a minimum working capacity of 3 days based on the normal flow rate.
10 |  | Injection is ensured by metering pumps, which is stopped/protected by tank low low level (to be finalized by package vendor.)
11 |  | Package Requirements
12 |  | Scope of supply and work shall include the complete system consisting of mainly the equipment, machinery, piping, electrical, instrument etc. but not limited to following items. (see detailes in next pages)
13 |  | - One Storage /Dilution Vessel (with mechanical agitator in case chemicals are supplied as solid or dilution is required): included in package Sec. 81-W-505.
14 |  | - Two Sets of Dosing Pumps: included in package Sec. 81-W-505 with discharge pulsation dampeners.
15 |  | - Each pump shall operate at all flow rates between 10 and 100% of design capacity
16 |  | - The injection pumps shall be design for 200% of the normal flow.
17 |  | - Connecting piping valves and accessories.
18 |  | - Required instrumentation and control for safe operation.
19 |  | -Discharge pulsation dampener for each pump individually.
20 |  | - One set of calibration pot (common for both pumps).
21 |  | - The vendor shall provide a skid mounted injection package Including above mentioned items to make sure package operates safetly
22 |  | and efficiently. This skid shall have proper facilities for maintenance, operation and easy transportation.
23 |  | NOTE: one common plant air driven portable loading pump shall be provided to transfer chemicals from barrels to tank.
24 |  | Package type A: Package type A is considered standalone package unit with no (or very limited) interface with DCS, ESD and F&G systems. (4)
25
26

## Content (3)
OWNER: |  |  |  | Pars Petrochemical Company | [24 empty] | contractor:
PROPANE DEHYDROGENATION (PDH) PROJECT
Duty Specification for Sodium Carbonate Dosing Package (81-W-505)
MC:
|  |  |  | Project code |  |  |  | Sec. |  |  |  | Phase Code |  |  |  | Department |  |  |  |  | Doc Type |  |  |  | Serial No.
Document Number : |  |  |  | 3981-050-DE-PR-DSP-018 | [24 empty] | Rev: |  |  | Page:
[29 empty] | 07 |  |  | 4 of 6
1 | Note | [32 empty] | Rev
2 |  | Item No. |  | 81-W-505 | [13 empty] | Service of Unit |  |  |  | Sodium Carbonate Dosing
3 |  | No.Required |  | Working |  |  | 1 |  | Standby |  |  | 0 |  | Total |  | 1 |  | Operation |  |  |  | Continuous
4 |  | Injection System for |  |  |  | Cooling Tower Package
5 |  | Liquid Injected |  |  |  | Sodium Carbonate
6
7 |  | INJECTION LIQUID
8 |  | Liquid |  | Sodium Carbonate Solution | [12 empty] | Temperature |  |  |  | Ambient | [11 empty] | C
9 |  | Injec. Flow | l/h |  | Nor. | Nor. | 18 |  | (1) |  | Rated | Rated | 36 |  | (1) |  | Specific Gravity |  |  |  |  | Kg/Lit |  |  | 1 ± 0.1 |  | (1), (14)
10 |  | Flow Rate to be Treated |  |  |  | 30000 |  |  |  |  | (1) |  |  |  | m3/h |  | Dosage |  |  | (1) |  |  |  | Viscosity | [5 empty] | (1) |  | centipoise
11 |  | Make Up Solvent |  |  |  | 15 |  |  |  |  | (1) |  |  |  | l/h |  | Vapour Pressure | [11 empty] | (1)
12 |  | Pressure Required at Injection Point | [6 empty] | 0 | [5 empty] | Bar(g) |  | Corrosive/Erosive Fluid | [5 empty] | Yes |  |  |  |  | / | No |  |  |  | (1)
13 | [16 empty] | Hazardous/Flammable/Toxic | [7 empty] | Yes |  | / | No |  | / | Yes |  | (1)
14 |  | INJECTION PUMP | [14 empty] | SOLUTION TANK
15 |  | Item No. | [14 empty] | Item No. | [9 empty] | No. Required |  |  |  | 1
16 |  | Service | Sodium Carbonate Dosing Pump | [13 empty] | Service |  |  |  | Sodium Carbonate Dosing Tank
17 |  | No. Required |  |  |  | Working |  |  | 1 |  | Standby |  |  | 1
18 |  | Flow Nor. |  |  | 18 | [5 empty] | (1) |  |  |  | l/h |  | Storage Time | [5 empty] | Day |  |  |  | 3 |  |  |  | (28)
19 |  | Flow Rated |  |  | 36 | [5 empty] | (1) |  |  |  | l/h |  | Capacity | [5 empty] | m3 |  |  |  | 1.5 |  |  |  | (1) (28)
20 |  | Press. At Discharge |  |  | 3 | [9 empty] | Bar(g) |  | Design Pressure | [5 empty] | Bar(g) |  |  |  | ATM+Full of Liquid
21 |  | Press. At Suction |  |  | ATM | [9 empty] | Bar(g) |  | Design Temp. | [5 empty] | C |  |  |  | 65 |  |  |  | (12)
22 |  | Type |  |  | Metering Pump | [11 empty] | Operating Press. | [5 empty] | Bar(g) |  |  |  | Atm.
23 |  | Cylinder/Case |  |  | Plastic Material (7) | [11 empty] | Operating Temp. | [5 empty] | C |  |  |  | Amb.
24 |  | Plunger/Int | [14 empty] | Type | [9 empty] | (3)
25 |  | Diaphragm | [14 empty] | Size | [5 empty] | mm |  |  |  | (3)
26 |  | BHP |  |  | (3) | [9 empty] | kW |  | Thickness | [5 empty] | mm |  |  |  | (3)
27 | [16 empty] | Buffer Tank Volume | [5 empty] | m3 |  |  |  | N/A |  | FALSE
28 |  | Capacity Control Mode |  |  |  |  | Manual | [9 empty] | Material | [5 empty] | FALSE |  |  |  | HDPE (1) |  | TRUE
29 |  | Capacity Control range % |  |  |  |  | 10-100 | [9 empty] | Accessories | [5 empty] | FALSE | [5 empty] | TRUE
30 |  | Capacity Control Type/Signal | [5 empty] | Local |  |  |  | / |  |  |  |  | FALSE | [5 empty] | NO | [5 empty] | NO
31 |  | Capacity Control |  |  |  |  | Stroke Adjustment | [9 empty] | NO | [5 empty] | NO | [5 empty] | FALSE
32 |  | Relief Valve Set. |  |  | barg |  | 4.5 | [9 empty] | NO | [8 empty] | NO
32 |  | Design Temp. |  |  | C |  | 65 | [5 empty] | (12) |  |  |  | Design Pressure |  |  |  |  | Bar(g) |  | 4.5
33 |  | AGITATOR
34 |  | Agitator Required |  |  | Yes | (1) |  | Item No. | [9 empty] | Service |  |  | Sodium Carbonate Tank Mixer
35 |  | No. Req'd. |  | 1 | [13 empty] | Mat. |  |  | HDPE (1)
36 |  | TRUE |  | Mechanical |  | TRUE | [5 empty] | TRUE | [7 empty] | TRUE | [6 empty] | TRUE
37 |  | ACCESSORIES (See sheet 5/6)
38 |  | TRUE |  |  |  | TRUE | [5 empty] | TRUE | [7 empty] | TRUE | [6 empty] | TRUE
39 |  | TRUE | [27 empty] | FALSE
40 |  | INSTALLATION | [27 empty] | TRUE
41 |  | Location |  | Under Shelter |  |  |  | (1) |  | Insulation Required |  |  |  |  | No |  | (1) |  | Steam / Electrical Tracing | [6 empty] | No |  |  | / | No |  |  | (1)
42 |  | Heating Cond. |  | Unheated | [5 empty] | (1) |  | Winterization Required | [6 empty] | No |  | Tropicalization Required | [5 empty] | Yes |  |  | TRUE
43 | [17 empty] | NACE Requirement | [5 empty] | NO
44 |  | Site AMB. Temp. |  |  | Min. |  |  |  | 5 |  |  | Max. |  | 48 | [5 empty] | C
45
Level Gague
Measuring Cup
Baffles
Floating Cover
Inner Basket
Steam Bubbling
Level Transmitter
Steam Heater
Electrical Heater
Strainers
Relief Valves
Pulsation Dampener
Calibration Pot
Pump Pressure Gauge
Sample Connection
Level Switch

## Content (2)
OWNER: | Pars Petrochemical Company | [5 empty] | contractor:
PROPANE DEHYDROGENATION (PDH) PROJECT
Duty Specification for Sodium Carbonate Dosing Package (81-W-505)
MC:
| Project code | Sec. | Phase Code | Department | Doc Type | Serial No.
Document Number : | 3981-050-DE-PR-DSP-018 | [5 empty] | Rev: | Page:
[7 empty] | 07 | 5 of 6
X4AO
X4AO

## Content (4)
OWNER: |  |  | Pars Petrochemical Company | [5 empty] | contractor:
PROPANE DEHYDROGENATION (PDH) PROJECT
Duty Specification for Sodium Carbonate Dosing Package (81-W-505)
MC:
|  |  | Project code | Sec. | Phase Code | Department | Doc Type | Serial No.
Document Number : |  |  | 3981-050-DE-PR-DSP-018 | [5 empty] | Rev: | Page:
[9 empty] | 07 | 6 of 6
1 | Note | [9 empty] | Rev
2 |  | Notes
3 |  | 1) To be finalized according to chemical Vendor's information. 2) DELETED 3) To be specified by package vendor. 4) Package type A is considered standalone package unit with no (or very limited) interface with DCS, ESD and F&G systems. For more details refer to : General Specification for Package Unit Control System "3981-00-BA-IN-SPC-021". 5) Injection point: Cooling Tower Basin. however its allowable to be recommended by the vendor. 6) Vessel elevation to be specified by vendor based on pump NPSH and piping requirement. 7) Minimum requirement. 8) For site condition and available utilities, refer to Process Design Basis (3981-00-BA-PR-BOD-008) and Site condition(3981-00-BA-PR-SPC-003) 9) For package battery limit refer to: PID NO. 3981-50-DE-PR-PID-002~004. 10) All equipments,line instruments shown within package limit are required as minimum and to be finalized By package vendor. 11) Pulsation dampener for pump suction shall be considered based on vendor recommendation. 12) In case of considering shelter for package. 13) DELETED 14) At amb. temp. 15) The dosing will be adjusted by means of the variable stroke adjustment either manually or automatically by signal from DCS. 16) Besides a stirrer, the tank must be provided with inlets for filling of chemicals and water. 17) Stroke shall be capable of being changed manually even during operation. 18) All the measures for seasonal condition changes shall be foreseen by vendor, taking into account the severe climatic conditions, 19) All the requirements for start-up or shut down (if any), to be advised by vendor 20) DELETED 21) DELETED 22) Equipment and machinery shall be provided so that the unit can operate for at least three years without major overhaul or inspection. 23) Block and bypass valves shall be provided for all control valves unless limited and restricted by Process nature and safety requirements. 24) Materials of construction and corrosion allowances shall be considered for a minimum of 25 years depreciation of the Sec. 25) DELETED 26) LT is required for solution tank 27) DELETED 28)To be confirmed by vendor,considering that minimum working capacity of 3 days based on the normal flow rate.
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23